## Slide 1: PLCopen - IEC 61131 - 3
Overview
Version 2.1, September 2006 PLCopen 2006
Notes: 1

## Slide 2: Table of contents
Advantages of IEC61131-3 for programmers
History and international standards 1970 to 1995
7 parts of the IEC 61131 standard
IEC 61131-3 software models
the 5 languages of the IEC 61131-3
Function blocks and POUs
IEC data types, standard functions and standard function blocks
PLCopen certification

## Slide 3: Table of contents - continued
PLCopen compliance levels
PLCopen training logo
PLCopen address

## Slide 4: Advantages of IEC 61131-3
International accepted standard
  Step by step all suppliers will support it
  Uniform structures, languages, and the way of handling
It saves you time
  Unique software model and data/ type concept
  You only have to learn it once for different controller types
  Reduced misunderstandings and errors
  Standard functions and function blocks
  Reusability of tested software
Notes: 3

## Slide 5: Advantages of IEC 61131-3
Supports safety and quality programming
  Easy and comfortable structuring
  Data typing prohibits programming errors
Provides the best language for each problem
  Consistent specifications of 5 languages
  Two textual and two graphical languages
  One structuring language, providing an overview
  Availability of high level language
  Possibility to mix different languages
Notes: 4

## Slide 6: International Language Standardisation
Source: Dr. J. Christensen
77
78
79
81
80
93
94
95
70
82
83
84
85
87
86
88
89
90
91
92
NEMA Programmable Controllers Committee formed (USA)
GRAFCET (France)
IEC 848, Function Charts
DIN 40719, Function Charts (Germany)
NEMA ICS-3-304, Programmable Controllers (USA)
IEC SC65A/WG6 formed
DIN 19 239, Programmable Controller (Germany)
MIL-STD-1815 Ada (USA)
IEC SC65A(Sec)67
Type 3 report recommendation
96
IEC 65A(Sec)38, Programmable Controllers
IEC 1131-3
IEC SC65A(Sec)49, PC Languages
IEC 64A(Sec)90
IEC 61131-3
name change
Notes: 5

## Slide 7: The 7 Parts of The IEC 61131 Standard
Part 1 General overview, definitions IS
Part 2 Hardware IS
Part 3 Programming Languages IS
Part 4 User Guidelines IS
Part 5 Communication IS
Part 7 Fuzzy Logic IS
Part 8 Technical Report
IS = International Standard
Notes: 6

## Slide 8: IEC 61131 - Part 1 - General Overview
Definitions and glossary of terms used in the standard
List of related / referenced IEC standards
Principal functional characteristics of programmable controller systems
Notes: 7

## Slide 9: IEC 61131 - Part 2 - Hardware
Electrical, mechanical and functional requirements for Programmable Controllers and associated peripherals
Service, storage and transportation conditions
Information to be supplied by manufacturer
Test methods and procedures for verification of compliance of programmable controllers and associated peripherals
Notes: 8

## Slide 10: IEC 61131 - Part 3 - Programming Languages
Software-, communication- and programming-model
Definition of five interlinked programming languages
Syntax and semantics of two textual and two graphical languages: Instruction List (IL), Structured Text (ST), Ladder Diagram (LD) and Function Block Diagram (FBD)
Sequential Function Chart (SFC) for program structuring
Notes: 9

## Slide 11: IEC 61131 - Part 4 User Guidelines
Assists the user in:
Utilizing the other parts of the programmable controller standard
Specifying the requirements for applications
Selecting and implementing systems
Notes: 10

## Slide 12: IEC 61131 - Part 5 Communication
Based on MMS (Manufacturing Message Specifications) (still in progress)
The provider is allowed to add more items!
Notes: 11

## Slide 13: IEC 61131 - Part 7 Fuzzy Logic
Provides the definition of fuzzy control sets
The provider is allowed to add more items!
Notes: 11

## Slide 14: IEC 61131 - Part 8 Technical Report
Provides guidelines for the application and implementation of programming languages for programmable controller
The provider is allowed to add more items!
Notes: 11

## Slide 15: IEC 61131-3 Software Model
Configuration A
FB2
Program P1
Program P2
Task1
Task2
Resource L
access paths
FB1
FB4
Program P3
Program P4
Task3
Task4
Resource L
FB3
global and direct adressed variables
Task association
Access path association
Notes: 12

## Slide 16: Definition of Software Model Terms
Configuration
  A language element corresponding to a programmable controller system
Resource
  A language element corresponding to a signal processing function and its human-machine interface and sensor actuator functions, like a CPU in your system
Task
  An execution control element providing for periodic or triggered execution of a group of associated program organization units
Program
  Highest level program organization unit, several in - and outputs possible, can call FBs and Functions
FB
  Program organization unit Function Block, several in - and outputs possible, can call other FBs and Functions
Notes: 13

## Slide 17
IEC 61131-3: The Common Elements
•
Character set (English.........)
•
Data types (BOOL, WORD, INTEGER.................)
•
Variables (VAR, VAR_input, VAR_output..........)
•
POUs,
Program Organisation Units (Function, Function Block...)
•
SFC Elements (Steps, Transitions.................................)
•
Configuration elements
:
(Tasks)
Basis for software re-use

## Slide 18
IEC 61131-3 Elementary Data Types
No. Keyword Data Type Bits
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
BOOL
SINT
INT
DINT
LINT
USINT
UINT
UDINT
ULINT
REAL
LREAL
TIME
DATE
TIME_OF_DAY
or TOD
DATE_AND_TIME
or DT
STRING
BYTE
WORD
DWORD
LWORD
Boolean
Short integer
Integer
Double integer
Long integer
Unsigned short integer
Unsigned integer
Unsigned double integer
Unsigned long integer
Real numbers
Long reals
Duration
Date (only)
Time of day (only)
Date and time of day
Character string
Bit string of length 8
Bit string of length 16
Bit string of length 32
Bit string of length 64
1
8
16
32
64
8
16
32
64
32
64
8
16
32
64

## Slide 19: The 5 Languages of IEC 61131-3
Instruction List Structured Text Sequential Function Chart
Function Block Diagram Ladder Diagram
LD A
ANDN B
ST C
C:= A AND NOT B
A B C
-| |--|/|----------------( )
AND
A C
B
Step 1 N FILL
Step 3
Step 2 S Empty
Transition 1
Transition 2
Notes: 15

## Slide 20: Ladder Diagram (LD)
Standardized, rationalized set of relay ladder programming symbols
Based on well-known US-style of programming, resembling electrical drawing standard
A B C
-| |--|/|----------------( )
Notes: 16

## Slide 21: Instruction List (IL)
Single Accumulator based execution model
Based upon the German ‘Anweisungsliste’, AWL
Only one operation such as storing a value in the accumulator register, is allowed per line
LD A
ANDN B
ST C
Notes: 17

## Slide 22: Structured Text (ST)
High level language, block structured
Syntax resembles PASCAL
Complex statements and nested instructions possible
Support for
  Iteration loops (REPEAT-UNTIL; WHILE-DO)
  Conditional execution (IF-THEN-ELSE; CASE)
  Functions (SQRT(), SIN())
C:= A AND NOT B
Notes: 18

## Slide 23: Function Block Diagram (FBD)
Graphical language, widely used in Europe
Allows program elements which appear as blocks to be "wired" together in a form analogous to a circuit diagram
Used in many applications that involve the flow of information or data between control components
AND
A C
B
Notes: 19

## Slide 24: Sequential Function Chart (SFC)
Graphical language which provides a diagrammatic representation of program sequences --> flowchart
Based on the French Grafcet (IEC 848)
Main structure and suitable for rapid diagnostics
The basic elements are steps with action blocks and transitions
Steps consist of a piece of program that is carried out until a condition specified in the transition is met
Programming of complex tasks by dividing in smaller parts
Each element can be programmed in any IEC- language
Step 1 N FILL
Step 3
Step 2 S Empty
Transition 1
Transition 2
Notes: 20

## Slide 25: POU = Program Organization Unit
POU’s enable re-use of software from macro level (Programs)
to micro level (FB and Functions).
A POU consists of a header (variable declaration) and the
body (instructions).
Notes: 22

## Slide 26: IEC 61131-3 Standard Datatypes
Bit string types (BOOL, BYTE, WORD, DWORD, LWORD)
Integer types (SINT, INT, DINT, LINT)
Unsigned integer types (USINT, UINT, UDINT, ULINT)
Real types (REAL, LREAL)
Time types (TIME, DATE, TIME_OF_DAY, DATE_AND_TIME)
Character types (STRING)
Vendor and user defined data types are possible
  Direct derived, sub range, enumeration
  Array, structure
Notes: 23

## Slide 27: IEC 61131-3 Standard Functions
Bit string functions (AND, OR, XOR, NOT, SHL, SHR, ROL, ROR)
Numerical functions (ADD, SUB, MUL, DIV, MOD, EXPT, ABS, SQRT, LN, LOG, EXP, SIN, COS, TAN, ASIN, ACOS, ATAN)
Type conversions (e.g. USINT_TO_DINT, BOOL_TO_BYTE)
Selection functions (SEL, MIN, MAX, LIMIT, MUX)
Comparison functions (GT, GE, EQ, LT, LE, NE)
String functions (LEN, LEFT, RIGHT, MID, CONCAT, INSERT, DELETE, REPLACE, FIND)
Vendor and user defined functions are possible
Notes: 24

## Slide 28: IEC 61131-3 Standard Function Blocks
Bistables (SR, RS, SEMA)
Edge detection (R_TRIG, F_TRIG)
Counters (CTU, CTD, CTUD)
Timers (TP, TON, TOF, RTC)
Vendor and user defined function blocks are possible
Notes: 25

## Slide 29: PLCopen
Mission
We want to be the leading association resolving topics related to control programming to support the use of international standards in this field.
Notes: 26

## Slide 30
PLCopen
PLCopen was founded on June 15, 1992 in Giessen, Germany.
Target was to promote IEC 61131-3, inform customers and give
more weight to the IEC 61131-3 standard.
PLCopen
Standardization in Industrial Control programming
TC6

## Slide 31: The Essence of Compliance without testing there is no standard
The IEC 61131 standard gives rules for compliancy
Certification gives guidance for users towards real IEC 61131-3 programming systems (e.g. PLCopen certified list shows compliant products)
Notes: 27

## Slide 32: PLCopen Compliance Level
To take away the confusion, PLCopen....
.... has defined 2 levels of compliance with a defined set of features
.... has defined an accreditation procedure
.... has accredited test institutes
.... developed test software, shared amongst members
.... has defined a certification procedure
.... and has members with certified products
This assures compliance now, and in the future.
Notes: 28

## Slide 33: PLCopen Compliance Levels
Application Program
FB
Variable
Code Body
FB
Variable
Code Body
FB
Variable
Code Body
Application Program
FB
Variable
Code Body
FB
Variable
Code Body
FB
Variable
Code Body
Conformity Level &
Reusability Level
Re-usability of Function (Block) libraries
Base Level
Portability of minimal systems
Notes: 29

## Slide 34: Compliance
Certified products
can use these logo’s
Notes: 30

## Slide 35: PLCopen Training Logo
Notes: 31

## Slide 36: PLCopen
P.O. Box 2015
NL 5300 CA Zaltbommel
The Netherlands
Tel: +31-418-541139
Fax: +31-418-516336
www.plcopen.org
Notes: 31